## ID-Serial
ArrayID | XML | HEX | Description | Decimal |  | Notes | Ref HEX | j3 | <- Enter Cell reference here to select required HEX string below
0 | STX | 02 | Start Transmission |  |  |  | j3 |  | 0200FE0648010B0A0D01FFFF191205040001FFFFFFFFFF0403FF01FFFFFFFFFFFFFFFFFFFFFFFF3134333131313032393932323020202043616C656E74612020202020202020200319120525A30104160EE614424D08920115230109780304020E2C1437502855
1 | HEADER | 00 | STRING SENT: Str1 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03, Str2 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 Str3 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03, Str4 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 Str5 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03, Str6 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 Str7 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03, Str8 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  |  |  | j3 |  | 0200FE0648010B0A0D01FFFF191205040001FFFFFFFFFF0403FF01FFFFFFFFFFFFFFFFFFFFFFFF3134333131313032393932323020202043616C656E74612020202020202020200319120525A30104160EE614424D08920115230109780304020E2C1437502855
2 |  | FE |  |  |  |  | j3
3 |  | 06 |  |  |  |  | j3
4 |  | 48 |  |  |  |  | j3
5 |  | 01 |  |  |  |  | j3
6 |  | 0B |  |  |  |  | j3
7 | 0 | 0A |  | 10 |  |  | j3
8 | 1 | 0D | dF-Code (decimal) | 13 |  |  | j3
9 | 2 | 01 | dU-Code (decimal) | 1 |  |  | j3
10 | 3 | FF |  | 255 |  |  | j3
11 | 4 | FF |  | 255 |  |  | j3
12 | 5 | 19 | Software Version (hex/10 = 1.9) | 25 |  |  | j3
13 | 6 | 12 | Parameter Version (hex/10 = 1.2) | 18 |  |  | j3
14 | 7 | 05 | Parameter Type (hex) | 5 |  |  | j3
15 | 8 | 04 |  | 4 |  |  | j3
16 | 9 | 00 |  | 0 |  |  | j3
17 | 10 | 01 |  | 1 |  |  | j3
18 | 11 | FF |  | 255 |  |  | j3
19 | 12 | FF |  | 255 |  |  | j3
20 | 13 | FF |  | 255 |  |  | j3
21 | 14 | FF |  | 255 |  |  | j3
22 | 15 | FF |  | 255 |  |  | j3
23 | 16 | 04 |  | 4 |  |  | j3
24 | 17 | 03 |  | 3 |  |  | j3
25 | 18 | FF |  | 255 |  |  | j3
26 | 19 | 01 |  | 1 |  |  | j3
27 | 20 | FF |  | 255 |  |  | j3
28 | 21 | FF |  | 255 |  |  | j3
29 | 22 | FF |  | 255 |  |  | j3
30 | 23 | FF |  | 255 |  |  | j3
31 | 24 | FF |  | 255 |  |  | j3
32 | 25 | FF |  | 255 |  |  | j3
33 | 26 | FF |  | 255 |  |  | j3
34 | 27 | FF |  | 255 |  |  | j3
35 | 28 | FF |  | 255 |  |  | j3
36 | 29 | FF |  | 255 |  |  | j3
37 | 30 | FF |  | 255 |  |  | j3
38 | 31 | FF |  | 255 |  |  | j3
39 | 32 | 31 | Boiler Serial 1431110299220 (concat ASCII) | 49 | 1 |  | j3
40 | 33 | 34 |  | 52 | 4 |  | j3
41 | 34 | 33 |  | 51 | 3 |  | j3
42 | 35 | 31 |  | 49 | 1 |  | j3
43 | 36 | 31 |  | 49 | 1 |  | j3
44 | 37 | 31 |  | 49 | 1 |  | j3
45 | 38 | 30 |  | 48 | 0 |  | j3
46 | 39 | 32 |  | 50 | 2 |  | j3
47 | 40 | 39 |  | 57 | 9 |  | j3
48 | 41 | 39 |  | 57 | 9 |  | j3
49 | 42 | 32 |  | 50 | 2 |  | j3
50 | 43 | 32 |  | 50 | 2 |  | j3
51 | 44 | 30 |  | 48 | 0 |  | j3
52 | 45 | 20 |  | 32 |  |  | j3
53 | 46 | 20 |  | 32 |  |  | j3
54 | 47 | 20 |  | 32 |  |  | j3
55 | 48 | 43 | Boiler Name = Calenta (concat ASCII) | 67 | C |  | j3
56 | 49 | 61 |  | 97 | a |  | j3
57 | 50 | 6C |  | 108 | l |  | j3
58 | 51 | 65 |  | 101 | e |  | j3
59 | 52 | 6E |  | 110 | n |  | j3
60 | 53 | 74 |  | 116 | t |  | j3
61 | 54 | 61 |  | 97 | a |  | j3
62 | 55 | 20 |  | 32 |  |  | j3
63 | 56 | 20 |  | 32 |  |  | j3
64 | 57 | 20 |  | 32 |  |  | j3
65 | 58 | 20 |  | 32 |  |  | j3
66 | 59 | 20 |  | 32 |  |  | j3
67 | 60 | 20 |  | 32 |  |  | j3
68 | 61 | 20 |  | 32 |  |  | j3
69 | 62 | 20 |  | 32 |  |  | j3
70 | 63 | 20 |  | 32 |  |  | j3
71 | 64 | 03 | PCU - Device Type (hex) | 3 |  |  | j3
72 | 65 | 19 | PCU - Software Version (hex/10 = 1.9) | 25 |  |  | j3
73 | 66 | 12 | PCU - Parameter Version (hex/10 = 1.2) | 18 |  |  | j3
74 | 67 | 05 | PCU - Parameter Type (hex) | 5 |  |  | j3
75 | 68 | 25 | Operating Hours ( =((E77*256)+E78)*2) | 37 | 19270 |  | j3
76 | 69 | A3 |  | 163 |  |  | j3
77 | 70 | 01 | PCU - Connected SU Type | 1 |  |  | j3
78 | 71 | 04 | PCU - Connected PSU Type | 4 |  |  | j3
79 | 72 | 16 | PCU - Last blocking code (decimal) | 22 |  |  | j3
80 | 73 | 0E | PCU - Last locking code (decimal) | 14 |  |  | j3
81 | 74 | E6 | PCU - Operating voltage (decimal) | 230 |  |  | j3
82 | 75 | 14 | Serial = 1442M0892 |  |  |  | j3
83 | 76 | 42 |  |  |  |  | j3
84 | 77 | 4D |  | 77 | M |  | j3
85 | 78 | 08 |  |  |  |  | j3
86 | 79 | 92 |  |  |  |  | j3
87 | 80 | 01 | Device Type (decimal) | 1 |  |  | j3
88 | 81 | 15 | Software Version (hex/10 = 1.5) |  |  |  | j3
89 | 82 | 23 | Parameter Version (hex/10 = 2.3) |  |  |  | j3
90 | 83 | 01 | Parameter Type (decimal) | 1 |  |  | j3
91 | 84 | 09 |  | 9 | 19392 |  | j3
92 | 85 | 78 |  | 120 |  |  | j3
93 | 86 | 03 | SU no. 1 - Connected PCU Type | 3 | connected PCU type |  | j3
94 | 87 | 04 | SU no. 1 - Connected PSU Type | 4 | Connected PSU type |  | j3
95 | 88 | 02 | SU no. 1 - Last blocking code | 2 | last blocking code |  | j3
96 | 89 | 0E | SU no. 1 - Last locking code | 14 | Last locking code |  | j3
97 | 90 | 2C | SU no. 1 - Last internal error | 44 | Last internal error |  | j3
98 | 91 | 14 | SU no. 1 Serial Number (concat) |  | 14 |  | j3
99 | 92 | 37 |  |  | 37 |  | j3
100 | 93 | 50 |  | 80 | P |  | j3
101 | 94 | 28 |  |  | 28 |  | j3
102 | 95 | 55 |  |  | 55 |  | j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
j3
|  |  | Send: |  |  | Response

## Samples
ArrayID | XML | HEX | Description | Hex2Dec | Decimal | Notes | Ref HEX | j5 | <- Enter Cell reference here to select required HEX string below
0 | STX | 02 | Start Transmission |  |  |  | j5 |  | 0241063E0200440ED40B82F34603CA124240510A00809E0CA00F008014051405449E0C003C006400000003C5000103FFFF000100000000000000000000002D03
1 | HEADER | 41 | STRING SENT: 0x02 0x52 0x05 0x06 0x02 0x00 0x53 0x03 |  |  |  | j5 |  | 0241063E0200410ED00B8BF34E03CA1242404F0A00809E0CA00F008014051405449E0C003C006400000003C5000103FFFF000100000000000000000000003303
2 |  | 06 |  |  |  |  | j5 |  | 0241063E0200430ED20B92F35003C91242404F0A00809E0CA00F008014051505459E0C003C006400000003C5000103FFFF000100000000000000000000003703
3 |  | 3E |  |  |  |  | j5 |  | 0241063E0200EC0E760CA8F3A401361042409A0B0080520DA00F00801405150542520D003C006400000003C5000103FFFF00010000000000000000000000D9030000000000000000480A10404E4D0500
4 |  | 02 |  |  |  |  | j5
5 |  | 00 |  |  |  |  | j5
6 | 0 | EC | Flow Temp | 236 | 38.2 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
7 | 1 | 0E |  | 14 |  |  | j5
8 | 2 | 76 | Return Temp | 118 | 31.9 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
9 | 3 | 0C |  | 12 |  |  | j5 |  | 0241063E02003615CE13A8F34803980D4240360B0080580CA00F008014051505488813004E006400000093C5080104FFFF0001000000000000000000000066030000000000000000480A10401BA50100
10 | 4 | A8 | DHW-in Temperature | 168 | -31.6 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
11 | 5 | F3 |  | 243 |  |  | j5
12 | 6 | A4 | Outside Temp | 164 | 4.2 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
13 | 7 | 01 |  | 1 |  |  | j5
14 | 8 | 36 | Calorifier Temperature | 54 | 41.5 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
15 | 9 | 10 |  | 16 |  |  | j5
16 | 10 | 42 |  |  |  | --- NOT IN USE --- | j5
17 | 11 | 40 |  |  |  | --- NOT IN USE --- | j5
18 | 12 | 9A | Boiler Control Temp B | 154 | 29.7 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
19 | 13 | 0B |  | 11 |  |  | j5
20 | 14 | 00 | Room Temp B | 0 | 0 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
21 | 15 | 80 |  | 128 |  |  | j5
22 | 16 | 52 | CH Setpoint B | 82 | 34.1 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
23 | 17 | 0D |  | 13 |  |  | j5
24 | 18 | A0 | DHW Setpoint B | 160 | 40 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
25 | 19 | 0F |  | 15 |  |  | j5
26 | 20 | 00 | Room Temp setpoint Opentherm B | 0 | 0 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
27 | 21 | 80 |  | 128 |  |  | j5
28 | 22 | 14 | Fan Speed setpoint B | 20 | 1300 | A.0+B.1 = (A*256)+B | j5
29 | 23 | 05 |  | 5 |  |  | j5
30 | 24 | 15 | Fan Speed B | 21 | 1301 | A.0+B.1 = (A*256)+B | j5
31 | 25 | 05 |  | 5 |  |  | j5
32 | 26 | 42 | Ionisation Current | 66 | 6.6 | uA*0.1 | j5
33 | 27 | 52 | Internal Setpoint B | 82 | 34.1 | SGN(A.0+B.1)*0.01 = ((A*256)+B)*0.01 | j5
34 | 28 | 0D |  | 13 |  |  | j5
35 | 29 | 00 | Available Power (Output) | 0 | 0 | A | j5
36 | 30 | 3C | Pump Percentage (Speed) | 60 | 60 | A | j5
37 | 31 | 00 |  |  |  | --- NOT IN USE --- | j5
38 | 32 | 64 | Desired Max Power (Required Output) | 100 | 100 | A | j5
39 | 33 | 00 | Actual Power from boiler | 0 | 0 | A | j5
40 | 34 | 00 |  |  |  | --- NOT IN USE --- | j5
41 | 35 | 00 |  |  |  | --- NOT IN USE --- | j5
42 | 36 | 03 | Various BIT Settings (Demand Source) | 3 | 00000011 | BIT0=Mod.Controller Connected, BIT1=Heat demand from Mod.Controller, BIT2=Heat demand from on/off controller, BIT3=Frost Protection, BIT4=DHW Eco, BIT5=DHW Blocking, BIT6=Anti Legionella, BIT7=DHW Heat Demand | j5
43 | 37 | C5 | Various BIT Settings (Input) | 197 | 11000101 | BIT0=Shudown Input, BIT1=Release Input, BIT2=Ionisation, BIT3=Flow Switch detecting DHW, BIT5=Min Gas Pressure, BIT6=CH Enable, BIT7=DHW Enable | j5
44 | 38 | 00 | Various BIT Settings (Valve) | 0 | 00000000 | BIT0=Gas Valve, BIT2=Ignition, BIT3=3-Way valve position, BIT4=Ext.3-Way Valve, BIT6=Ext. Gas Valve | j5
45 | 39 | 01 | Various BIT Settings (Pump) | 1 | 00000001 | BIT0=Pump, BIT1=Calorifier Pump, BIT2=Ext.CH Pump, BIT4=Status Report, BIT7=Opentherm SmartPower | j5
46 | 40 | 03 | State | 3 | 3 | 3:Burning CH | j5
47 | 41 | FF | Lockout E | 255 | 255 | No locking | j5
48 | 42 | FF | Blocking b | 255 | 255 | No blocking | j5
49 | 43 | 00 | Sub-State | 0 | 0 | 0:Standby | j5
50 | 44 | 01 |  |  |  | name.nr="2533" description.nr="2533", BIT2 | j5
51 | 45 | 00 |  |  |  | --- NOT IN USE --- | j5
52 | 46 | 00 |  |  |  | --- NOT IN USE --- | j5
53 | 47 | 00 |  |  |  | --- NOT IN USE --- | j5
54 | 48 | 00 |  |  |  | --- NOT IN USE --- | j5
55 | 49 | 00 |  |  |  | --- NOT IN USE --- | j5
56 | 50 | 00 |  |  |  | --- NOT IN USE --- | j5
57 | 51 | 00 |  |  |  | --- NOT IN USE --- | j5
58 | 52 | 00 |  |  |  | --- NOT IN USE --- | j5
59 | 53 | 00 |  |  |  | --- NOT IN USE --- | j5
60 | 54 | 00 |  |  |  | --- NOT IN USE --- | j5
61 | 55 | 00 |  |  |  | --- NOT IN USE --- | j5
62 | 56 | D9 | CRC |  |  | CRC | j5
63 | 57 | 03 | End Transmission |  |  |  | j5
State - Lookup |  |  |  | Lockout - Lookup
0 | 0:Standby |  |  | 0 | PSU not connected (Locking 0)
1 | 1:Boiler start |  |  | 1 | SU parameter fault (Locking 1)
2 | 2:Burner start |  |  | 2 | 02:T Flow closed
3 | 3:Burning CH |  |  | 3 | 03:T Flow open
4 | 4:Burning DHW |  |  | 4 | 04:T Flow < min.
5 | 5:Burner stop |  |  | 5 | 05:T Flow > max.
6 | 6:Boiler stop |  |  | 6 | T Return closed (Locking 6)
7 | 7:- |  |  | 7 | T Return open (Locking 7)
8 | 8:Controlled stop |  |  | 8 | T Return < min. (Locking 8)
9 | 9:Blocking mode |  |  | 9 | T Return > max. (Locking 9)
10 | 10:Locking mode |  |  | 10 | 10:dT(Flow,Return) > max.
11 | 11:Chimney mode L |  |  | 11 | 11:dT(Return,Flow) > max.
12 | 12:Chimney mode h |  |  | 12 | STB activated (Locking 12)
13 | 13:Chimney mode H |  |  | 14 | 5x Unsuccessful start (Locking 14)
14 | 14:- |  |  | 16 | False flame (Locking 16)
15 | 15:Manual-heatdemand |  |  | 17 | SU Gasvalve driver error (Locking 17)
16 | 16:Boiler-frost-protection |  |  | 34 | Fan out of control range (Locking 34)
17 | 17:De-airation |  |  | 35 | Return over Flow temp. (Locking 35)
999 | Unknown State |  |  | 36 | 5x Flame loss (Locking 36)
|  |  |  | 37 | SU communication (Locking 37)
Sub-Status |  |  |  | 38 | SCU-S communication (Locking 38)
0 | 0:Standby |  |  | 39 | BL input as lockout (Locking 39)
1 | 1:Anti-cycling |  |  | 40 | - (Locking 40)
2 | 2:Open hydraulic valve |  |  | 255 | No locking
3 | 3:Pump start |  |  | 999 | Unknown locking code
4 | 4:Wait for burner start
10 | 10:Open external gas valve |  |  | Blocking - Lookup
11 | 11:Fan to fluegasvalve speed |  |  | 0 | PCU parameter fault (Blocking 0)
12 | 12:Open fluegasvalve |  |  | 1 | T Flow > max.(Blocking 1)
13 | 13:Pre-purge |  |  | 2 | dT/s Flow > max. (Blocking 2)
14 | 14:Wait for release |  |  | 7 | dT(Flow,Return) > max.(Blocking 7)
15 | 15:Burner start |  |  | 8 | No release signal(Blocking 8)
16 | 16:VPS test |  |  | 9 | L-N swept(Blocking 9)
17 | 17:Pre-ignition |  |  | 10 | Blocking signal ex frost(Blocking 10)
18 | 18:Ignition |  |  | 11 | Blocking signal inc frost(Blocking 11)
19 | 19:Flame check |  |  | 13 | SCU communication(Blocking 13)
20 | 20:Interpurge |  |  | 14 | Min. water pressure(Blocking 14)
30 | 30:Normal internal setpoint |  |  | 15 | Min. gas pressure(Blocking 15)
31 | 31:Limited internal setpoint |  |  | 16 | Ident. SU mismatch(Blocking 16)
32 | 32:Normal power control |  |  | 17 | Ident. dF/dU table error(Blocking 17)
33 | 33:Gradient control level 1 |  |  | 18 | Ident. PSU mismatch(Blocking 18)
34 | 34:Gradient control level 2 |  |  | 19 | Ident. dF/dU needed(Blocking 19)
35 | 35:Gradient control level 3 |  |  | 20 | Identification running(Blocking 20)
36 | 36:Flame protection |  |  | 21 | SU communications lost(Blocking 21)
37 | 37:Stabilization time |  |  | 22 | Flame lost(Blocking 22)
38 | 38:Cold start |  |  | 25 | Internal SU error(Blocking 25)
39 | 39:Limited power Tfg |  |  | 26 | Calorifier sensor error(Blocking 26)
40 | 40:Burner stop |  |  | 27 | DHW in sensor error(Blocking 27)
41 | 41:Post purge |  |  | 255 | No blocking
42 | 42:Fan to fluegasvalve speed |  |  | 999 | Unknown blocking code
43 | 43:Close fluegasvalve
44 | 44:Stop fan
45 | 45:Close external gas valve
60 | 60:Pump post running
61 | 61:Pump stop
62 | 62:Close hydraulic valve
63 | 63:Start anti-cycle timer
255 | 255:Reset wait time
999 | Unknown Sub-State

## Counters
ArrayID | XML | HEX | Description | Hex2Dec | Decimal | Notes |  |  | Resp1-1C | Resp2-1D | Resp3-1E | Resp4-1F
0 | STX | 2 | Start Transmission | [5 empty] | 2 | 2 | 2 | 2 | 024106161001251105000000 0620 0044 04BA 0058 0858 A503 F0A7 C64B | Counter1
1 | HEADER | 41 | STRING SENT: Str1 = 0x02 0x52 0x05 0x06 0x10 0x02 0x43 0x03 Str2 = 0x02 0x52 0x05 0x06 0x10 0x01 0x40 0x03 |  |  |  |  | START | 02 | 02 | 0 | 0 | 024106161002 0414 0034 0080 022A 0000 0000 0000 0000 CF03 4336 3442 | Counter2
2 |  | 06 | [5 empty] | HEADER | 41 | 41 | FE | FE
3 |  | 16 | [6 empty] | 06 | 06 | 6 | 6
4 |  | 10 | [6 empty] | 16 | 16 | 18 | 18
5 |  | 02 | [6 empty] | 10 | 10 | 10 | 10
7 | 0 | 20 |  | 32 |  | --- NOT IN USE --- |  | messge # | 02 | 01 | 1E | 1F
8 |  | 10 |  | 16 |  | --- NOT IN USE --- |  | 0 | 21 | 20 | 0 | 0
9 | 2 | 03 |  | 3 |  | --- NOT IN USE --- |  | 1 | 25 | 10 | 0 | 0
10 |  | 0F |  | 15 |  | --- NOT IN USE --- |  | 2 | 19 | 03 | 0 | 0
11 | 4 | 00 |  | 0 |  | --- NOT IN USE --- |  | 3 | F9 | 0F | 0 | 0
12 | 6 | 6 | Hours run pump CH+DHW | 6 | 3160 | (A.1+B.0)*2 | C | 5 | 2C | 00 | 0 | 0
13 |  | 2C |  | 44 |  |  | O | 6 | 1E | 29 | 0 | 0
14 | 8 | 0 | Hours run 3-way valve DHW | 0 | 136 | (A.1+B.0)*2 | U | 7 | 95 | 45 | 0 | 0
15 |  | 44 |  | 68 |  |  | N | 8 | 00 | 01 | 0 | 0
16 | 10 | 4 | Hours run CH+DHW | 4 | 2420 | (A.1+B.0)*2 | T | 9 | B0 | D0 | 0 | 0
17 |  | BA |  | 186 |  |  | E | 10 | 01 | 23 | 0 | 0
18 | 12 | 0 | Hours run DHW | 0 | 88 | (A.1+B.0) | R | 11 | 0F | EE | 0 | 0
19 |  | 58 |  | 88 |  |  | 1 | 12 | 00 | 03 | 0 | 0
20 | 14 | 8 | Power Supply available hours | 8 | 4272 | (A.1+B.0)*2 |  | 13 | 00 | ED | 0 | 0
21 |  | 58 |  | 88 |  |  |  | 14 | 00 | 98 | 0 | 0
7 | 16 | 4 | Pump starts CH+DHW | 4 | 8352 | (A.1+B.0)*8 | C | 15 | 00 | DC | 0 | 0
8 |  | 14 |  | 20 |  |  | O | CRC | B7 | A6 | 93 | C2
9 | 18 | 0 | Number of 3-Way valve cycles | 0 | 416 | (A.1+B.0)*8 | U | END | 03 | 03 | 7D | ED
10 |  | 34 |  | 52 |  |  | N |  | 3 | 3 | 3 | 3
11 | 20 | 0 | Burner Starts DHW A | 0 | 1024 | (A.1+B.0)*8 | T | 16 |  | 21
12 |  | 80 |  | 128 |  |  | E | 17 |  | 25
13 | 22 | 2 | Total Burner Starts CH+DHW A | 2 | 4432 | (A.1+B.0)*8 | R | 18 |  | 19
14 |  | 2A |  | 42 |  |  | 2 | 19 |  | F9
15 | 24 | 0 | Failed burner starts A | 0 | 0 | (A.1+B.0) |  | 20 |  | 09
16 |  | 0 |  | 0 |  |  |  | 21 |  | 2C
17 | 26 | 0 | Number of flame loss A | 0 | 0 | (A.1+B.0) |  | 22 |  | 1E
18 |  | 0 |  | 0 |  |  |  | 23 |  | 95
|  | 00 |  | 0 |  | --- NOT IN USE --- |  | 24 |  | 00
|  | 00 |  | 0 |  | --- NOT IN USE --- |  | 25 |  | B0
|  | 00 |  | 0 |  | --- NOT IN USE --- |  | 26 |  | 01
|  | 00 |  | 0 |  | --- NOT IN USE --- |  | 27 |  | 0F
|  | 0 |  | 0 |  | --- NOT IN USE --- |  | 28 |  | 00
|  | 0 |  | 0 |  | --- NOT IN USE --- |  | 29 |  | 00
|  | 0 |  | 0 |  | --- NOT IN USE --- |  | 30 |  | 00
|  | 0 |  | 0 |  | --- NOT IN USE --- |  | 31 |  | 00
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | 0 |  | 0 |  | --- NOT IN USE ---
|  | ** Note** | Looks like only Str1 and Str2 are needed - others return NULL

## Parameters
ArrayID | XML | HEX | Description | Decimal | Notes | Ref HEX | I2 | <- Enter Cell reference here to select required HEX string below
0 | STX | 02 | Start Transmission |  |  | I2 |  | 0241061610034C3C01020001FFFFFFFFFFFFFFFFFFFF23350D190000FFFFFFFFFFFFFFFFFFFF03020528140505024646140F010F19060A55070B020514010A0F0FFF1B6363EF
1 | HEADER | 41 | STRING SENT: Str1 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03, Str2 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 Str3 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03, Str4 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 Str5 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03, Str6 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 Str7 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03, Str8 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  |  | I2
2 |  | 06 |  |  |  | I2
3 |  | 16 |  |  |  | I2
4 |  | 10 |  |  |  | I2
5 |  | 03 |  |  |  | I2
7 | 0 | 4C | Max flow temperature during CH mode | 76 | °C | I2
8 | 1 | 3C | Desired DHW temperature | 60 | °C | I2
9 | 2 | 01 | Switch on/off CH/DHW function | 1 | 0:CH Off DHW Off; 1:CH On DHW On; 2:CH On DHW Off; 3:CH Off DHW On | I2
10 | 3 | 02 | Keeping warm for DHW comfort | 2 | 0: Always On; 1:Always Off; 2:Controller | I2
11 | 4 | 00 | Anticipation current on/off thermostat | 0 | 0:No; 1:Yes | I2
12 | 5 | 01 | Display auto off after 3 min. | 1 | 0:No; 1:Yes | I2
13 | 6 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
14 | 7 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
15 | 8 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
16 | 9 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
17 | 10 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
18 | 11 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
19 | 12 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
20 | 13 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
21 | 14 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
22 | 15 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
23 | 16 | 23 | Max fanspeed during CH mode | 3500 | A x 100 RPM | I2
24 | 17 | 35 | Max fanspeed during DHW mode | 5300 | A x 100 RPM | I2
25 | 18 | 0D | Max fanspeed during CH+DHW mode | 1300 | A x 100 RPM (max 2500?) | I2
26 | 19 | 19 | Offset on partload fanspeed | 25 | RPM | I2
27 | 20 | 00 | Pump speed for CH mode | 0 | 0:Low; 1:High | I2
28 | 21 | 00 | HRU connected to shut down input | 0 | 0:No; 1:Yes | I2
29 | 22 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
30 | 23 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
31 | 24 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
32 | 25 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
33 | 26 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
34 | 27 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
35 | 28 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
36 | 29 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
37 | 30 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
38 | 31 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
39 | 32 | 03 | Turn on delay for DHW detection | 0.3 | /10 sec | I2
40 | 33 | 02 | Hysterese when warming up for DHW comfort | 2 | °C | I2
41 | 34 | 05 | Offset DHW | 5 | °C | I2
42 | 35 | 28 | P factor for DHW in control band DHWset | 40 |  | I2
43 | 36 | 14 | I factor for DHW in control band DHWset | 20 |  | I2
44 | 37 | 05 | Temperature range for modulating on DHWset | 5 | °C | I2
45 | 38 | 05 | P factor for CH control when T1>setpoint | 5 |  | I2
46 | 39 | 02 | I factor for CH control when T1>setpoint | 2 |  | I2
47 | 40 | 46 | Absolute max fan speed CH | 7000 | A x 100 RPM | I2
48 | 41 | 46 | Absolute max fan speed DHW | 7000 | A x 100 RPM | I2
49 | 42 | 14 | Control band DHW | 20 |  | I2
50 | 43 | 0F | Waiting time pump for prehaet plate heat exchanger | 1.5 | /10 sec | I2
51 | 44 | 01 | Postpump time CH | 100 | min | I2
52 | 45 | 0F | Postpump time DHW | 15 | seconds | I2
53 | 46 | 19 | Modulate back when dT > this par | 25 | °C | I2
54 | 47 | 06 | Forced part load for CH and DHW->CH | 6 | *10s | I2
55 | 48 | 0A | Start when T<Tset+5-this param at CH | 10 | °C | I2
56 | 49 | 55 | Time between warming up starts boiler | 85 | min | I2
57 | 50 | 07 | Warm up interval for DHW after CH | 7 | min | I2
58 | 51 | 0B | Offset when warming up for DHW comfort | 11 | °C | I2
59 | 52 | 02 | Hystereses DHW | 2 | °C | I2
60 | 53 | 05 | T corr. DHW for Tset, ww - Tret, plate heat exch. | 5 | °C | I2
61 | 54 | 14 | Max. flow temp during CH operation | 20 | °C | I2
62 | 55 | 01 | P factor CH control | 1 |  | I2
63 | 56 | 0A | I factor CH control | 10 |  | I2
64 | 57 | 0F | P factor DHW | 15 |  | I2
65 | 58 | 0F | I factor DHW | 15 |  | I2
66 | 59 | FF | --- NOT IN USE --- | 255 | --- NOT IN USE --- | I2
67 | 60 | 1B | Shut down when temp increase > this param | 27 | °C | I2
68 | 61 | 63 | Max. fan speed increase | 99 | RPM/s | I2
69 | 62 | 63 | Max. fan speed decrease | 99 | RPM/s | I2
70 | 63 | EF | --- NOT IN USE --- | 239 | --- NOT IN USE --- | I2
71 | 64 |  | Number of de-airation cycles on startup | 0 |  | I2
72 | 65 |  | Maximum gradient for decreasing modulation | 0 | 0.01 °C/second | I2
73 | 66 |  | Maximum gradient for forced minimal load | 0 | 0.01 °C/second | I2
74 | 67 |  | Maximum gradient for blocking | 0 | 0.01 °C/second | I2
75 | 68 |  | Maximum temperature difference between flow & return | 0 | °C | I2
76 | 69 |  | Modulate back when dT > this par | 0 | °C | I2
77 | 70 |  | Pump control range dT for CH | 0 | °C | I2
78 | 71 |  | Pump control CH on start heat demand | 0 | % | I2
79 | 72 |  | Start hysteresis for CH | 0 | °C | I2
80 | 73 |  | Stabilisation time after burner start CH | 0 | seconds | I2
81 | 74 |  | Minimum burner anti-cycle time | 0 | minutes | I2
82 | 75 |  | Maximum burner anti-cycle time | 0 | minutes | I2
83 | 76 |  | Absolute maximum fan speed CH | 0 | A x 100 RPM | I2
84 | 77 |  | Absolute maximum fan speed DHW | 0 | A x 100 RPM | I2
85 | 78 |  | Pump control, control range dT for DHW | 0 | °C | I2
86 | 79 |  | Pump control, DHW minimum speed | 0 | % | I2
87 | 80 |  | Pump control, DHW maximum speed | 0 | % | I2
88 | 81 |  | Pump control, DHW on start DHW demand | 0 | % | I2
89 | 82 |  | Warm up interval for DHW after CH | 0 | minutes | I2
90 | 83 |  | Time between warming up starts boiler | 0 | minutes | I2
91 | 84 |  | Hysterese when warming up for DHW comfort | 0 | °C | I2
92 | 85 |  | Offset when warming up for DHW comfort | 0 | SGN(A) °C - [Signed 8bit] | I2
93 | 86 |  | DHW start raise depending on DHW flow | 0 |  | I2
94 | 87 |  | Switch on hystereses DHW operation | 0 | °C | I2
95 | 88 |  | Offset DHW | 0 | °C | I2
96 | 89 |  | T correction DHW for Tset, ww - Tret, plate heat exchanger | 0 | °C | I2
97 | 90 |  | %Tf/Tr for DHW control temp at pumpspeed 20% | 0 | % | I2
98 | 91 |  | %Tf/Tr for DHW control temp at pumpspeed 100% | 0 | % | I2
99 | 92 |  | Waiting time pump for preheat plate heat exchanger | 0 | per 10 seconds | I2
100 | 93 |  | Postpump time DHW | 0 | seconds | I2
101 | 94 |  | Correction factor DHW pulses to l/min | 0 | per second | I2
102 | 95 |  | Min DHW flow for DHW detection | 0 | A x 0.1 litres/minute | I2
103 | 96 |  | Type of sensor for DHW detection | 0 | 0:DHW flow sensor; 1:DHW flow switch | I2
104 | 97 |  | Factor for dynamic flow detection | 0 |  | I2
105 | 98 |  | DHW stabilisation time for pump modulation | 0 | /10 seconds | I2
106 | 99 |  | DHW gradient for stabilisation time pump | 0 | 0.01 °C/second | I2
107 | 100 |  | Range in which the DHW booster is disabled | 0 | °C | I2
108 | 101 |  | P-Factor for booster on start DHW | 0 |  | I2
109 | 102 |  | P-Factor for feedforward on flow DHW | 0 |  | I2
110 | 103 |  | P-Factor for booster on flow changes DHW | 0 |  | I2
111 | 104 |  | Switch off offset calorifier sensor | 0 | °C | I2
112 | 105 |  | Switch on delay DHW pump in comparison with boiler pump | 0 | SGN(A) °C - [Signed 8bit] | I2
113 | 106 |  | Post pump time DHW | 0 | seconds | I2
114 | 107 |  | Pre-purge time for burner start | 0 | seconds | I2
115 | 108 |  | Post-purge time for burner stop | 0 | seconds | I2
116 | 109 |  | Maximum flow temperature for blocking | 0 | °C | I2
117 | 110 |  | Tacho pulses per revolution of the fan | 0 | per second | I2
118 | 111 |  | P-factor fan speed control | 0 |  | I2
119 | 112 |  | I-factor fan speed control | 0 |  | I2
120 | 113 |  | P-factor CH control | 0 |  | I2
121 | 114 |  | I-factor CH control | 0 |  | I2
122 | 115 |  | P-factor for CH control when T1>setpoint | 0 |  | I2
123 | 116 |  | I-factor for CH control when T1>setpoint | 0 |  | I2
124 | 117 |  | P-factor DHW control | 0 |  | I2
125 | 118 |  | I-factor DHW control | 0 |  | I2
126 | 119 |  | I-factor for pump control on CH | 0 |  | I2
127 | 120 |  | I-factor for pump control on DHW | 0 |  | I2
128 | 121 |  | RPM at theoreteical 0KW | 0 |  | I2
129 | 122 |  | Power output (KW) at theoretical 10,000RPM | 0 |  | I2
130 | 123 |  | PWM value red for normal display backlight | 0 | Think this will allow change to display colour based on RGB colours (e.g. 0000FF=Blue, FF0000=Red, FF00FF=Magenta, 800000=Maroon, 800080=Purple, etc. | I2
131 | 124 |  | PWM value blue for normal display backlight | 0 |  | I2
132 | 125 |  | PWM value green for normal display backlight | 0 |  | I2
133 | 126 |  | --- NOT IN USE --- | 0 | --- NOT IN USE --- | I2
134 | 127 |  | --- NOT IN USE --- | 0 | --- NOT IN USE --- | I2
|  |  | Send: |  | Response
|  |  | 0x02 0x52 0x05 0x06 0x10 0x03 0x42 0x03 |  | 0241061610034C3C01020001FFFFFFFFFFFFFFFFFFFF3003
|  |  | 0x02 0x52 0x05 0x06 0x10 0x04 0x45 0x03 |  | 02410616100423350D190000FFFFFFFFFFFFFFFFFFFF4703
|  |  | 0x02 0x52 0x05 0x06 0x10 0x05 0x44 0x03 |  | 02410616100503020528140505024646140F010F19067403
|  |  | 0x02 0x52 0x05 0x06 0x10 0x06 0x47 0x03 |  | 0241061610060A55070B020514010A0F0FFF1B6363EF0703
0200FE06181014413C010200020501FFFFFFFFFFFFFFFF299103

## Parameters-org
ArrayID | XML | HEX | Description | Decimal | Notes |  | Resp1-14 | Resp2-15 | Resp3-16 | Resp4-17 | Resp5-18 | Resp6-19 | Resp7-1A | Resp8-1B
0 | STX | 2 | Start Transmission |  |  | START | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
1 | HEADER | 0 | STRING SENT: Str1 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03, Str2 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 Str3 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03, Str4 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 Str5 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03, Str6 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 Str7 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03, Str8 = 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  |  | HEADER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | fe | bar: Resp1-14 to Resp8-1B
3 |  | 6 |  |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
4 |  | 18 |  |  |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
5 |  | 10 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
6 |  | 14 |  |  |  |  | 14 | 15 | 16 | 17 | 18 | 19 | 1a | 1b
7 | 0 | 41 | Max flow temperature during CH mode | 65 | °C | 0 | 41 | 2a | 4 | ff | 1 | 50 | 0 | 1a
8 | 1 | 3c | Desired DHW temperature | 60 | °C | 1 | 3c | 44 | 0 | ff | 28 | 39 | 78 | 1
9 | 2 | 1 | Switch on/off CH/DHW function | 1 | 0:CH Off DHW Off; 1:CH On DHW On; 2:CH On DHW Off; 3:CH Off DHW On | 2 | 1 | 11 | 0 | ff | 46 | 7 | 64 | 0a
10 | 3 | 2 | Comfort DHW | 2 | 0: Always On; 1:Always Off; 2:Controller | 3 | 2 | 4b | 1 | ff | 5a | 54 | 0a | 5
11 | 4 | 0 | Anticipation current on/off thermostat | 0 | 0:No; 1:Yes | 4 | 0 | 28 | 1 | ff | 32 | 5 | 6 | 2
12 | 5 | 2 | Amount of information on display | 2 | 0:Simple; 1:Extended; 2:Automatic; 3:Automatic+Key Lock | 5 | 2 | 8 | 0 | ff | 19 | 0 | 1e | 14
13 | 6 | 5 | Pump Post Run time | 5 | minutes | 6 | 5 | 5a | 0 | ff | 5 | 0f | 28 | 28
14 | 7 | 1 | Display brightness when backlight active | 1 | 0:Low; 1:Bright | 7 | 1 | ff | 1 | ff | 1e | 2 | 4b | 14
15 | 8 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 8 | ff | 14 | 0 | ff | 0a | 5 | 0 | 1e
16 | 9 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 9 | ff | 14 | 0 | ff | 1e | 6 | fe | 7a
17 | 10 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 10 | ff | f1 | 0 | c8 | 3 | 32 | 0a | 0a
18 | 11 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 11 | ff | 2 | 1 | 2 | 9 | 19 | 0 | 0
19 | 12 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 12 | ff | 6 | af | 0 | 44 | 0 | 0a | ff
20 | 13 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 13 | ff | f6 | 1e | 23 | 44 | 1 | 64 | 0
21 | 14 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 14 | ff | 0 | 23 | 13 | 28 | b3 | 2 | 0c
22 | 15 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE --- | 15 | ff | 14 | ff | 22 | 14 | 9 | 28 | 1a
23 | 16 | 2a | Max fanspeed during CH mode | 4200 | A x 100 RPM | CRC | 29 | 3e | c1 | 11 | bc | 52 | 22 | e4
24 | 17 | 44 | Max fanspeed during DHW mode | 6800 | A x 100 RPM | CRC | 91 | 66 | 0c | bb | 43 | 34 | 7f | cd
25 | 18 | 11 | Max fanspeed during CH+DHW mode | 1700 | A x 100 RPM | END | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
26 | 19 | 4b | Offset on partload fanspeed | 75 | RPM
27 | 20 | 28 | Fan speed at boiler start | 4000 | A x 100 RPM
28 | 21 | 8 | Minimum waterpressure for notification | 0.8 | A x 0.1 bar
29 | 22 | 5a | Maximum flow temperature for heating system | 90 | °C
30 | 23 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
31 | 24 | 14 | Footpoint heating curve outside temperature | 20 | °C
32 | 25 | 14 | Footpoint heating curve flow temperature | 20 | °C
33 | 26 | f1 | Clima point heating curve outside temperature | -15 | SGN(A) °C - [Signed 8bit]
34 | 27 | 2 | Pump CH Min | 20 | A x 10%
35 | 28 | 6 | Pump CH Max | 60 | A x 10%
36 | 29 | f6 | Minimum outside temperature for frost protection | -10 | SGN(A) °C - [Signed 8bit]
37 | 30 | 0 | Legionella Protection | 0 | 0:No; 1:Yes; 2:Controller
38 | 31 | 14 | Setpoint raise at warming up calorifier | 20 | °C
39 | 32 | 4 | Switch on hystereses calorifier sensor | 4 | °C
40 | 33 | 0 | 3-Way valve standby: CH or DHW | 0 | 0:CH, 1:DHW
41 | 34 | 0 | Boiler type | 0 | 0:Combi ; 1:Solo(+boiler); 2:Comfort Column
42 | 35 | 1 | Function of blocking input | 1 | 0:CH enable; 1:Blocking without frost protection; 2:Blocking with frost protection; 3:Locking with frost protection
43 | 36 | 1 | Function of release input | 1 | 0:DHW enable; 1:Burner release
44 | 37 | 0 | Wait time for valid release signal, 0=no check | 0 | seconds
45 | 38 | 0 | Wait time for fluegas valve | 0 | seconds
46 | 39 | 1 | Position from alarm/operation signal relay | 1 | 0:Operation Signal; 1:Failure signal
47 | 40 | 0 | Min gas pressure detection | 0 | 0:No; 1:Yes
48 | 41 | 0 | HRU connected | 0 | 0:No; 1:Yes
49 | 42 | 0 | Mains L-N phase detection activated | 0 | 0:No; 1:Yes
50 | 43 | 1 | Service Notification for boiler dependant maint. | 1 | 0:Off; 1:ABC; 2:Custom
51 | 44 | af | Service Hours for boiler connected to mains supply | 17500 | A x 100 hours (17500h = ~729 days = ~2 years)
52 | 45 | 1e | Service Hours for boiler burner | 3000 | A x 100 hours 3000h = ~125 days but not based on 24hours/day)
53 | 46 | 23 | Tau factor for average flow temperature calculation | 35 | seconds
54 | 47 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
55 | 48 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
56 | 49 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
57 | 50 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
58 | 51 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
59 | 52 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
60 | 53 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
61 | 54 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
62 | 55 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
63 | 56 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
64 | 57 | ff | --- NOT IN USE --- | 255 | --- NOT IN USE ---
65 | 58 | c8 | DHW-in gradient for restart stabilisation time | 2 | 0.01 °C/second
66 | 59 | 2 | dT pump offset | 2 | °C
67 | 60 | 0 | Offset control temp | 0 | SGN(A) /10 °C [Signed 8bit]
68 | 61 | 23 | DHW Flow at minimum output power | 3.5 | A x 0.1 litres/minute
69 | 62 | 13 | --- NOT IN USE --- | 19 | --- NOT IN USE ---
70 | 63 | 22 | --- NOT IN USE --- | 34 | --- NOT IN USE ---
71 | 64 | 1 | Number of de-airation cycles on startup | 1
72 | 65 | 28 | Maximum gradient for decreasing modulation | 0.4 | 0.01 °C/second
73 | 66 | 46 | Maximum gradient for forced minimal load | 0.7 | 0.01 °C/second
74 | 67 | 5a | Maximum gradient for blocking | 0.9 | 0.01 °C/second
75 | 68 | 32 | Maximum temperature difference between flow & return | 50 | °C
76 | 69 | 19 | Modulate back when dT > this par | 25 | °C
77 | 70 | 5 | Pump control range dT for CH | 5 | °C
78 | 71 | 1e | Pump control CH on start heat demand | 30 | %
79 | 72 | 0a | Start hysteresis for CH | 10 | °C
80 | 73 | 1e | Stabilisation time after burner start CH | 30 | seconds
81 | 74 | 3 | Minimum burner anti-cycle time | 3 | minutes
82 | 75 | 9 | Maximum burner anti-cycle time | 9 | minutes
83 | 76 | 44 | Absolute maximum fan speed CH | 6800 | A x 100 RPM
84 | 77 | 44 | Absolute maximum fan speed DHW | 6800 | A x 100 RPM
85 | 78 | 28 | Pump control, control range dT for DHW | 40 | °C
86 | 79 | 14 | Pump control, DHW minimum speed | 20 | %
87 | 80 | 50 | Pump control, DHW maximum speed | 80 | %
88 | 81 | 39 | Pump control, DHW on start DHW demand | 57 | %
89 | 82 | 7 | Warm up interval for DHW after CH | 7 | minutes
90 | 83 | 54 | Time between warming up starts boiler | 84 | minutes
91 | 84 | 5 | Hysterese when warming up for DHW comfort | 5 | °C
92 | 85 | 0 | Offset when warming up for DHW comfort | 0 | SGN(A) °C - [Signed 8bit]
93 | 86 | 0f | DHW start raise depending on DHW flow | 15
94 | 87 | 2 | Switch on hystereses DHW operation | 2 | °C
95 | 88 | 5 | Offset DHW | 5 | °C
96 | 89 | 6 | T correction DHW for Tset, ww - Tret, plate heat exchanger | 6 | °C
97 | 90 | 32 | %Tf/Tr for DHW control temp at pumpspeed 20% | 50 | %
98 | 91 | 19 | %Tf/Tr for DHW control temp at pumpspeed 100% | 25 | %
99 | 92 | 0 | Waiting time pump for preheat plate heat exchanger | 0 | per 10 seconds
100 | 93 | 1 | Postpump time DHW | 1 | seconds
101 | 94 | b3 | Correction factor DHW pulses to l/min | 179 | per second
102 | 95 | 9 | Min DHW flow for DHW detection | 0.9 | A x 0.1 litres/minute
103 | 96 | 0 | Type of sensor for DHW detection | 0 | 0:DHW flow sensor; 1:DHW flow switch
104 | 97 | 78 | Factor for dynamic flow detection | 120
105 | 98 | 64 | DHW stabilisation time for pump modulation | 10 | /10 seconds
106 | 99 | 0a | DHW gradient for stabilisation time pump | 0.1 | 0.01 °C/second
107 | 100 | 6 | Range in which the DHW booster is disabled | 6 | °C
108 | 101 | 1e | P-Factor for booster on start DHW | 30
109 | 102 | 28 | P-Factor for feedforward on flow DHW | 40
110 | 103 | 4b | P-Factor for booster on flow changes DHW | 75
111 | 104 | 0 | Switch off offset calorifier sensor | 0 | °C
112 | 105 | fe | Switch on delay DHW pump in comparison with boiler pump | -2 | SGN(A) °C - [Signed 8bit]
113 | 106 | 0a | Post pump time DHW | 10 | seconds
114 | 107 | 0 | Pre-purge time for burner start | 0 | seconds
115 | 108 | 0a | Post-purge time for burner stop | 10 | seconds
116 | 109 | 64 | Maximum flow temperature for blocking | 100 | °C
117 | 110 | 2 | Tacho pulses per revolution of the fan | 2 | per second
118 | 111 | 28 | P-factor fan speed control | 40
119 | 112 | 1a | I-factor fan speed control | 26
120 | 113 | 1 | P-factor CH control | 1
121 | 114 | 0a | I-factor CH control | 10
122 | 115 | 5 | P-factor for CH control when T1>setpoint | 5
123 | 116 | 2 | I-factor for CH control when T1>setpoint | 2
124 | 117 | 14 | P-factor DHW control | 20
125 | 118 | 28 | I-factor DHW control | 40
126 | 119 | 14 | I-factor for pump control on CH | 20
127 | 120 | 1e | I-factor for pump control on DHW | 30
128 | 121 | 7a | RPM at theoreteical 0KW | 122
129 | 122 | 0a | Power output (KW) at theoretical 10,000RPM | 10
130 | 123 | 0 | PWM value red for normal display backlight | 0 | Think this will allow change to display colour based on RGB colours (e.g. 0000FF=Blue, FF0000=Red, FF00FF=Magenta, 800000=Maroon, 800080=Purple, etc.
131 | 124 | ff | PWM value blue for normal display backlight | 255
132 | 125 | 0 | PWM value green for normal display backlight | 0
133 | 126 | 0c | --- NOT IN USE --- | 12 | --- NOT IN USE ---
134 | 127 | 1a | --- NOT IN USE --- | 26 | --- NOT IN USE ---
|  |  | Send: |  | Response
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x14 0x99 0x04 0x03 |  | 0200fe06181014413c010200020501ffffffffffffffff299103
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x15 0x58 0xC4 0x03 |  | 0200fe061810152a44114b28085aff1414f10206f600143e6603
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x16 0x18 0xC5 0x03 |  | 0200fe06181016040000010100000100000001af1e23ffc10c03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x17 0xD9 0x05 0x03 |  | 0200fe06181017ffffffffffffffffffffc8020023132211bb03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x18 0x99 0x01 0x03 |  | 0200fe061810180128465a3219051e0a1e030944442814bc4303
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x19 0x58 0xC1 0x03 |  | 0200fe061810195039075405000f02050632190001b309523403
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x1A 0x18 0xC0 0x03 |  | 0200fe0618101a0078640a061e284b00fe0a000a640228227f03
|  |  | 0x02 0xFE 0x00 0x05 0x08 0x10 0x1B 0xD9 0x00 0x03 |  | 0200fe0618101b1a010a05021428141e7a0a00ff000c1ae4cd03

## Sheet1
Type | Group | Name | Description | Byte | Number | expression | Format
field | 1 | dF-code | dF-code | 1 |  | A | 0
field | 1 | dU-code | dU-code | 2 |  | A | 0
field | 1 | Software version | Software version | 5 | 6
field | 1 | Parameter version | Parameter version | 6 | 6
field | 1 | Parameter type | Parameter type | 7 |  | A | 0
select | 1 | Next Service code | Next Service code | 10 |  | A | 0
field | 1 | Serial number | Serial number | 32 | 4
field | 1 | Boiler name | Boiler name | 48 | 4
field | 2 | Device type | Device type | 0 |  | A | 0
field | 2 | Software version | Software version | 1 | 6
field | 2 | Parameter version | Parameter version | 2 | 6
field | 2 | Parameter type | Parameter type | 3 |  | A | 0
field | 2 | Operating hours | Operating hours | 4 |  | (A.1 + B.0) x 2 | 0
field | 2 | Connected SU type | Connected SU type | 6 |  | A | 0
field | 2 | Connected PSU type | Connected PSU type | 7 |  | A | 0
field | 2 | Last blocking code | Last blocking code | 8 |  | A | 0
field | 2 | Last locking code | Last locking code | 9 |  | A | 0
field | 2 | Operating Voltage | Operating Voltage | 10 |  | A | 0
field | 2 | Serial number | Serial number | 11 | 5
field | 3 | Device type | Device type | 0 |  | A | 0
field | 3 | Software version | Software version | 1 | 6
field | 3 | Parameter version | Parameter version | 2 | 6
field | 3 | Parameter type | Parameter type | 3 |  | A | 0
field | 3 | Operating hours | Operating hours | 4 |  | (A.1 + B.0) x 8 | 0
field | 3 | Connected PCU type | Connected PCU type | 6 |  | A | 0
field | 3 | Connected PSU type | Connected PSU type | 7 |  | A | 0
field | 3 | Last blocking code | Last blocking code | 8 |  | A | 0
field | 3 | Last locking code | Last locking code | 9 |  | A | 0
field | 3 | Last internal error | Last internal error | 10 |  | A | 0
field | 3 | Serial number | Serial number | 11 | 5
field | 4 | Device type | Device type | 0 |  | A | 0
field | 4 | Software version | Software version | 1 | 6
field | 4 | Operating hours | Operating hours | 4 |  | (A.1 + B.0) x 8 | 0
field | 4 | Serial number | Serial number | 11 | 5

## P1_V5 Sample
Odczyt danych Sample
P1_V5
| reads |  | write (string sends)
| 022065: 2021-03-27 20:16:34,7462245 +0,0288021 |  | 021954: 2021-03-27 20:16:33,7756456 +0,0000532
| 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 | .A.......%...... | 07 42 A0 00 05 40 D2 07 42 A0 00 05 40 D2 07 42 | .B ..@Ň.B ..@Ň.B
02410616010B07000025110500000000002016300595FB03 | 00 20 16 30 05 95 FB 03 | . .0.•ű. | A0 00 05 40 D2 02 52 05 06 01 0B 5B 03 | ..@Ň.R....[.
0241061610100A08081A17020A0A060C020B0B0808065A03
| 022217: 2021-03-27 20:16:34,8472291 +0,0628601 |  | 022214: 2021-03-27 20:16:34,7830269 +0,0000501
0241063E0200440ED40B82F34603CA124240510A00809E0CA00F008014051405449E0C003C006400000003C5000103FFFF000100000000000000000000002D03
0241063E0200410ED00B8BF34E03CA1242404F0A00809E0CA00F008014051405449E0C003C006400000003C5000103FFFF000100000000000000000000003303 | 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C | .A.............. | 02 52 05 06 10 10 51 03 | .R....Q.
0241063E0200430ED20B92F35003C91242404F0A00809E0CA00F008014051505459E0C003C006400000003C5000103FFFF000100000000000000000000003703 | 02 0B 0B 08 08 06 5A 03 | ......Z.
0241063E0200480ED00B93F34B03CA124240500A00809E0CA00F008014051505449E0C003C006400000003C5000103FFFF000100000000000000000000003903
0241063E0200450ED00B8EF34A03CA124240500A00809E0CA00F008014051405459E0C003C006400000003C5000103FFFF000100000000000000000000002803 |  |  | 022440: 2021-03-27 20:16:38,6108231 +0,0000533
0241063E0200440ED60B8EF34803C8124240520A00809E0CA00F008014051505459E0C003C006400000003C5000103FFFF000100000000000000000000002C03 | 022443: 2021-03-27 20:16:38,6504890 +0,0388645
0241063E0200420ED60B96F34603CA1242404E0A00809E0CA00F008014051505449E0C003C006400000003C5000103FFFF000100000000000000000000002303 |  |  | 02 52 05 06 02 00 53 03 | .R....S.
0241063E0200420ED60B93F34803CA124240500A00809E0CA00F008014051405449E0C003C006400000003C5000103FFFF000100000000000000000000003703 | 02 41 06 3E 02 00 44 0E D4 0B 82 F3 46 03 CA 12 | .A.>..D.Ô.‚óF.Ę.
0241063E0200420ED00B8EF34B03CA1242404F0A00809E0CA00F008014051405459E0C003C006400000003C5000103FFFF000100000000000000000000003103 | 42 40 51 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@Q..€ž. ..€....
0241063E0200430ED40B8CF34803C91242404F0A00809E0CA00F008014051305449E0C003C006400000003C5000103FFFF000100000000000000000000003003 | 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙ | 022832: 2021-03-27 20:16:39,6153742 +0,0000511
0241063E0200410ED40B94F34603CA1242404F0A00809E0CA00F008014051405449E0C003C006400000003C5000103FFFF000100000000000000000000002003 | FF 00 01 00 00 00 00 00 00 00 00 00 00 00 2D 03 | ˙.............-.
0241063E0200440ED00B8DF34803C8124240500A00809E0CA00F008014051405459E0C003C006400000003C5000103FFFF000100000000000000000000002A03 |  |  | 02 52 05 06 02 00 53 03 | .R....S.
0241063E0200420ED00B8DF34C03C81242404F0A00809E0CA00F008014051405459E0C003C006400000003C5000103FFFF000100000000000000000000003703
0241063E0200420ED60B95F34703CA124240500A00809E0CA00F008014051305449E0C003C006400000003C5000103FFFF000100000000000000000000003903 | 022835: 2021-03-27 20:16:39,6495540 +0,0328688
0241063E0200430ED60B92F34A03CA124240500A00809E0CA00F008014051405449E0C003C006400000003C5000103FFFF000100000000000000000000003503 |  |  | 023224: 2021-03-27 20:16:40,6032863 +0,0000509
0241063E0200440ED40B92F34603CB124240500A00809E0CA00F008014051505439E0C003C006400000003C5000103FFFF000100000000000000000000003B03 | 02 41 06 3E 02 00 41 0E D0 0B 8B F3 4E 03 CA 12 | .A.>..A.Đ.‹óN.Ę.
| 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@O..€ž. ..€.... | 02 52 05 06 02 00 53 03 | .R....S.
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 33 03 | ˙.............3.
023616: 2021-03-27 20:16:41,6114851 +0,0000517
| 023227: 2021-03-27 20:16:40,6496263 +0,0448423 |  | 02 52 05 06 02 00 53 03 | .R....S.
| 02 41 06 3E 02 00 43 0E D2 0B 92 F3 50 03 C9 12 | .A.>..C.Ň.’óP.É. |  |  | 02 41 06 3E 02 00 43 0E D2 0B 92 F3 50 03 C9 12 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 37 03
| 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 | B@O..€ž. ..€.... | 024008: 2021-03-27 20:16:42,6158883 +0,0000560
| 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Ež..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 37 03 | ˙.............7. | 02 52 05 06 02 00 53 03 | .R....S.
| 023619: 2021-03-27 20:16:41,6517459 +0,0388730 |  | 024400: 2021-03-27 20:16:43,6061274 +0,0000511
| 02 41 06 3E 02 00 48 0E D0 0B 93 F3 4B 03 CA 12 | .A.>..H.Đ.“óK.Ę. | 02 52 05 06 02 00 53 03 | .R....S. | 02 41 06 3E 02 00 48 0E D0 0B 93 F3 4B 03 CA 12 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 39 03
| 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 | B@P..€ž. ..€....
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 39 03 | ˙.............9. | 024792: 2021-03-27 20:16:44,6111776 +0,0000522
|  |  | 02 52 05 06 02 00 53 03 | .R....S.
024011: 2021-03-27 20:16:42,6508179 +0,0338728
| 02 41 06 3E 02 00 45 0E D0 0B 8E F3 4A 03 CA 12 | .A.>..E.Đ.ŽóJ.Ę. | 025184: 2021-03-27 20:16:45,6162150 +0,0000526 |  | 02 41 06 3E 02 00 45 0E D0 0B 8E F3 4A 03 CA 12 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 28 03
| 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@P..€ž. ..€....
| 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Ež..<.d....Ĺ...˙ | 02 52 05 06 02 00 53 03 | .R....S.
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 28 03 | ˙.............(.
025576: 2021-03-27 20:16:46,6201425 +0,0000511
024403: 2021-03-27 20:16:43,6519071 +0,0448718
|  |  | 02 52 05 06 02 00 53 03 | .R....S.
| 02 41 06 3E 02 00 44 0E D6 0B 8E F3 48 03 C8 12 | .A.>..D.Ö.ŽóH.Č. |  |  | 02 41 06 3E 02 00 44 0E D6 0B 8E F3 48 03 C8 12 42 40 52 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 2C 03
| 42 40 52 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 | B@R..€ž. ..€....
| 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Ež..<.d....Ĺ...˙ | 025968: 2021-03-27 20:16:47,6294148 +0,0000517
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 2C 03 | ˙.............,.
|  |  | 02 52 05 06 02 00 53 03 | .R....S.
024795: 2021-03-27 20:16:44,6529064 +0,0408251
026360: 2021-03-27 20:16:48,6173749 +0,0000536
| 02 41 06 3E 02 00 42 0E D6 0B 96 F3 46 03 CA 12 | .A.>..B.Ö.–óF.Ę. |  |  | 02 41 06 3E 02 00 42 0E D6 0B 96 F3 46 03 CA 12 42 40 4E 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 23 03
| 42 40 4E 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 | B@N..€ž. ..€.... | 02 52 05 06 02 00 53 03 | .R....S.
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 23 03 | ˙.............#.
026752: 2021-03-27 20:16:49,6232188 +0,0000513
| 025187: 2021-03-27 20:16:45,6519816 +0,0348762 |  | 02 52 05 06 02 00 53 03 | .R....S.
| 02 41 06 3E 02 00 42 0E D6 0B 93 F3 48 03 CA 12 | .A.>..B.Ö.“óH.Ę. |  |  | 02 41 06 3E 02 00 42 0E D6 0B 93 F3 48 03 CA 12 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 37 03
| 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@P..€ž. ..€.... | 027144: 2021-03-27 20:16:50,6295044 +0,0000525
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 37 03 | ˙.............7. | 02 52 05 06 02 00 53 03 | .R....S.
| 025579: 2021-03-27 20:16:46,6520411 +0,0308488 |  | 027536: 2021-03-27 20:16:51,6201820 +0,0000519
| 02 41 06 3E 02 00 42 0E D0 0B 8E F3 4B 03 CA 12 | .A.>..B.Đ.ŽóK.Ę. | 02 52 05 06 02 00 53 03 | .R....S. | 02 41 06 3E 02 00 42 0E D0 0B 8E F3 4B 03 CA 12 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 31 03
| 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@O..€ž. ..€....
| 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Ež..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 31 03 | ˙.............1. | 027928: 2021-03-27 20:16:52,6270904 +0,0000549
|  |  | 02 52 05 06 02 00 53 03 | .R....S.
025971: 2021-03-27 20:16:47,6541218 +0,0238740
| 02 41 06 3E 02 00 43 0E D4 0B 8C F3 48 03 C9 12 | .A.>..C.Ô.ŚóH.É. | 028320: 2021-03-27 20:16:53,6155248 +0,0000519 |  | 02 41 06 3E 02 00 43 0E D4 0B 8C F3 48 03 C9 12 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 13 05 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 30 03
| 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 13 05 | B@O..€ž. ..€....
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙ | 02 52 05 06 02 00 53 03 | .R....S.
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 30 03 | ˙.............0.
026363: 2021-03-27 20:16:48,6531858 +0,0348723
| 02 41 06 3E 02 00 41 0E D4 0B 94 F3 46 03 CA 12 | .A.>..A.Ô.”óF.Ę. |  |  | 02 41 06 3E 02 00 41 0E D4 0B 94 F3 46 03 CA 12 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 20 03
| 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@O..€ž. ..€....
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 20 03 | ˙............. .
026755: 2021-03-27 20:16:49,6532564 +0,0288731
| 02 41 06 3E 02 00 44 0E D0 0B 8D F3 48 03 C8 12 | .A.>..D.Đ.ŤóH.Č. |  |  | 02 41 06 3E 02 00 44 0E D0 0B 8D F3 48 03 C8 12 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 2A 03
| 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@P..€ž. ..€....
| 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Ež..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 2A 03 | ˙.............*.
027147: 2021-03-27 20:16:50,6543198 +0,0238680
| 02 41 06 3E 02 00 42 0E D0 0B 8D F3 4C 03 C8 12 | .A.>..B.Đ.ŤóL.Č. |  |  | 02 41 06 3E 02 00 42 0E D0 0B 8D F3 4C 03 C8 12 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 37 03
| 42 40 4F 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@O..€ž. ..€....
| 45 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Ež..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 37 03 | ˙.............7.
027539: 2021-03-27 20:16:51,6533907 +0,0318724
| 02 41 06 3E 02 00 42 0E D6 0B 95 F3 47 03 CA 12 | .A.>..B.Ö.•óG.Ę. |  |  | 02 41 06 3E 02 00 42 0E D6 0B 95 F3 47 03 CA 12 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 13 05 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 39 03
| 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 13 05 | B@P..€ž. ..€....
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 39 03 | ˙.............9.
027931: 2021-03-27 20:16:52,6754655 +0,0478535
| 02 41 06 3E 02 00 43 0E D6 0B 92 F3 4A 03 CA 12 | .A.>..C.Ö.’óJ.Ę. |  |  | 02 41 06 3E 02 00 43 0E D6 0B 92 F3 4A 03 CA 12 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 35 03
| 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 14 05 | B@P..€ž. ..€....
| 44 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Dž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 35 03 | ˙.............5.
028323: 2021-03-27 20:16:53,6755333 +0,0588698
| 02 41 06 3E 02 00 44 0E D4 0B 92 F3 46 03 CB 12 | .A.>..D.Ô.’óF.Ë. |  |  | 02 41 06 3E 02 00 44 0E D4 0B 92 F3 46 03 CB 12 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 43 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF FF 00 01 00 00 00 00 00 00 00 00 00 00 00 3B 03
| 42 40 50 0A 00 80 9E 0C A0 0F 00 80 14 05 15 05 | B@P..€ž. ..€....
| 43 9E 0C 00 3C 00 64 00 00 00 03 C5 00 01 03 FF | Cž..<.d....Ĺ...˙
| FF 00 01 00 00 00 00 00 00 00 00 00 00 00 3B 03 | ˙.............;.
028715: 2021-03-27 20:16:54,6746071 +0,0558058

## P1_V5 ID
Identyfikacja | reads |  | writes STRING SENT:
02410616010B07000025110500000000002016300595FB03 | 018859: 2021-03-27 20:05:38,2326416 +0,0964575 |  | 018856: 2021-03-27 20:05:38,1350354 +0,0000516
0241061610100A08081A17020A0A060C020B0B0808065A03
02410616010B07000025110500000000002016300595FB03 | 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 | .A.......%...... | 02 52 05 06 01 0B 5B 03 | .R....[.
0241061610100A08081A17020A0A060C020B0B0808065A03 | 00 20 16 30 05 95 FB 03 | . .0.•ű. |  |  | 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 00 20 16 30 05 95 FB 03
018996: 2021-03-27 20:05:38,2699079 +0,0000267
018999: 2021-03-27 20:05:38,3336200 +0,0628948
|  |  | 02 52 05 06 10 10 51 03 | .R....Q.
| 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C | .A..............
| 02 0B 0B 08 08 06 5A 03 | ......Z. |  |  | 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C 02 0B 0B 08 08 06 5A 03
019144: 2021-03-27 20:05:38,3954539 +0,0000259
| 019147: 2021-03-27 20:05:38,4326282 +0,0358667 |  | 02 52 05 06 01 0B 5B 03 | .R....[.
| 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 | .A.......%......
| 00 20 16 30 05 95 FB 03 | . .0.•ű. | 019296: 2021-03-27 20:05:38,4698772 +0,0000334 |  | 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 00 20 16 30 05 95 FB 03
|  |  | 02 52 05 06 10 10 51 03 | .R....Q.
019299: 2021-03-27 20:05:38,5326368 +0,0619052
| 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C | .A..............
| 02 0B 0B 08 08 06 5A 03 | ......Z. |  |  | 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C 02 0B 0B 08 08 06 5A 03
02410616010B07000025110500000000002016300595FB03 0241061610100A08081A17020A0A060C020B0B0808065A03 02410616010B07000025110500000000002016300595FB03 0241061610100A08081A17020A0A060C020B0B0808065A03

## Parameters P1_V5
Parameters
02410616010B07000025110500000000002016300595FB03 | reads Response |  | writes Send
0241061610100A08081A17020A0A060C020B0B0808065A03 | 020363: 2021-03-27 20:12:27,1439905 +0,0417109 |  | 019448: 2021-03-27 20:10:29,0297576 +0,0000259
024106161003372901020102FFFFFFFFFFFFFFFF4E3C2E03
0241061610042F2F0D1900020000000821140F010A056F03 | 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 | .A.......%...... | 02 52 05 06 01 0B 5B 03 | .R....[. | 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 00 20 16 30 05 95 FB 03
02410616100505022F3214462102071E01041B0A14063003 | 00 20 16 30 05 95 FB 03 | . .0.•ű.
024106161006000F14050A0514010A0F0F0F141032057503
019600: 2021-03-27 20:10:29,1291364 +0,0000718
020515: 2021-03-27 20:12:27,2439945 +0,0609118
|  |  | 02 52 05 06 10 10 51 03 | .R....Q.
| 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C | .A.............. |  |  | 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C 02 0B 0B 08 08 06 5A 03
| 02 0B 0B 08 08 06 5A 03 | ......Z.
019752: 2021-03-27 20:10:29,2557661 +0,0000303
| 020667: 2021-03-27 20:12:27,3439719 +0,0339482 |  | 02 52 05 06 10 03 42 03 | .R....B.
| 02 41 06 16 10 03 37 29 01 02 01 02 FF FF FF FF | .A....7)....˙˙˙˙ |  |  | 02 41 06 16 10 03 37 29 01 02 01 02 FF FF FF FF FF FF FF FF 4E 3C 2E 03
| FF FF FF FF 4E 3C 2E 03 | ˙˙˙˙N<.. | 019904: 2021-03-27 20:10:29,3278423 +0,0000249
|  |  | 02 52 05 06 10 04 45 03 | .R....E.
020819: 2021-03-27 20:12:27,4449874 +0,0629127
| 02 41 06 16 10 04 2F 2F 0D 19 00 02 00 00 00 08 | .A....//........ | 020056: 2021-03-27 20:10:29,4298462 +0,0000256 |  | 02 41 06 16 10 04 2F 2F 0D 19 00 02 00 00 00 08 21 14 0F 01 0A 05 6F 03
| 21 14 0F 01 0A 05 6F 03 | !.....o.
|  |  | 02 52 05 06 10 05 44 03 | .R....D.
020971: 2021-03-27 20:12:27,5439819 +0,0608834
020208: 2021-03-27 20:10:29,5289083 +0,0000273
| 02 41 06 16 10 05 05 02 2F 32 14 46 21 02 07 1E | .A....../2.F!... |  |  | 02 41 06 16 10 05 05 02 2F 32 14 46 21 02 07 1E 01 04 1B 0A 14 06 30 03
| 01 04 1B 0A 14 06 30 03 | ......0. | 02 52 05 06 10 06 47 03 | .R....G.
021123: 2021-03-27 20:12:27,6440101 +0,0619385
| 02 41 06 16 10 06 00 0F 14 05 0A 05 14 01 0A 0F | .A.............. |  |  | 02 41 06 16 10 06 00 0F 14 05 0A 05 14 01 0A 0F 0F 0F 14 10 32 05 75 03
| 0F 0F 14 10 32 05 75 03 | ....2.u.
02410616010B07000025110500000000002016300595FB03 0241061610100A08081A17020A0A060C020B0B0808065A03 024106161003372901020102FFFFFFFFFFFFFFFF4E3C2E03 0241061610042F2F0D1900020000000821140F010A056F03 02410616100505022F3214462102071E01041B0A14063003 024106161006000F14050A0514010A0F0F0F141032057503
02410616010B07000025110500000000002016300595FB030241061610100A08081A17020A0A060C020B0B0808065A03024106161003372901020102FFFFFFFFFFFFFFFF4E3C2E030241061610042F2F0D1900020000000821140F010A056F0302410616100505022F3214462102071E01041B0A14063003024106161006000F14050A0514010A0F0F0F141032057503

## Counters P1_V5
Counter
| reads |  | writes
02410616010B07000025110500000000002016300595FB03 | 000925: 2021-03-28 17:33:28,4565624 +0,0588120 |  | 000922: 2021-03-28 17:33:28,3966073 +0,0000355 |  | 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 00 20 16 30 05 95 FB 03
0241061610100A08081A17020A0A060C020B0B0808065A03
024106161001251105000000061A004404B60058084E8503 | 02 41 06 16 01 0B 07 00 00 25 11 05 00 00 00 00 | .A.......%...... | 02 52 05 06 01 0B 5B 03 | .R....[.
02410616100204140034008002280000000000000000CD03 | 00 20 16 30 05 95 FB 03 | . .0.•ű.
001074: 2021-03-28 17:33:28,4937054 +0,0000224
02410616100204140034008002280000000000000000CD03F0A7C64B | 001077: 2021-03-28 17:33:28,5566760 +0,0620466 |  |  |  | 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C 02 0B 0B 08 08 06 5A 03
|  |  | 02 52 05 06 10 10 51 03 | .R....Q.
| 02 41 06 16 10 10 0A 08 08 1A 17 02 0A 0A 06 0C | .A..............
| 02 0B 0B 08 08 06 5A 03 | ......Z.
001226: 2021-03-28 17:33:28,6465108 +0,0000266
| 001229: 2021-03-28 17:33:28,7566002 +0,1089492 |  | 02 52 05 06 10 01 40 03 | .R....@. | 02 41 06 16 10 01 25 11 05 00 00 00 06 1A 00 44 04 B6 00 58 08 4E 85 03
| 02 41 06 16 10 01 25 11 05 00 00 00 06 1A 00 44 | .A....%........D
| 04 B6 00 58 08 4E 85 03 | .¶.X.N…. | 001378: 2021-03-28 17:33:28,7947241 +0,0000247
|  |  | 02 52 05 06 10 02 43 03 | .R....C.
| 001381: 2021-03-28 17:33:28,8566934 +0,0609944 |  |  |  | 02 41 06 16 10 02 04 14 00 34 00 80 02 28 00 00 00 00 00 00 00 00 CD 03
02 41 06 16 10 02 04 14 00 34 00 80 02 28 00 00
00 00 00 00 00 00 CD 03
Str1 = 0x02 0x52 0x05 0x06 0x10 0x02 0x43 0x03
Str2 = 0x02 0x52 0x05 0x06 0x10 0x01 0x40 0x03

## Arkusz2
02410616010B07000025110500000000002016300595FB03
0241061610100A08081A17020A0A060C020B0B0808065A03
024106161001251105000000061A004404B60058084E8503
02410616100204140034008002280000000000000000CD03
Calenta | 0x02, 0xFE, 0x01, 0x05, 0x08, 0x02, 0x01, 0x69, 0xAB, 0x03
Avanta | 0x02, 0x52, 0x05, 0x06, 0x02, 0x00, 0x53, 0x03
02 52 05 06 02 00 53 03
Calenta | 0x02, 0xFE, 0x00, 0x05, 0x08, 0x10, 0x1C, 0x98, 0xC2, 0x03 | Str1 = 0x02 0x52 0x05 0x06 0x10 0x02 0x43 0x03
Str2 = 0x02 0x52 0x05 0x06 0x10 0x01 0x40 0x03
Str1 = | 0x02, 0x52, 0x05, 0x06, 0x10, 0x02, 0x43, 0x03
02 52 05 06 10 02 43 03
Calenta | 0x02, 0xFE, 0x00, 0x05, 0x08, 0x10, 0x1D, 0x59, 0x02, 0x03
Str2 = | 0x02, 0x52, 0x05, 0x06, 0x10, 0x01, 0x40, 0x03
02 52 05 06 10 01 40 03